## Design Operating Data
Power Station
Unit No
Clarification |  |  | Unit
Manufacturer |  | Turbine
Generator
Boiler
Load |  | Maxiumum Load | MW
|  | Minimum Load | MW
Hear Rate |  | Power Produced heat rate at Maximum load | Kcal/KWh
|  | Power transmitted heat reat at miximum Load | Kcal/KWh
الاستهلاك الذاتي للوحدة |  | Auxilary power consumption (%) | %
معدل استهلاك الوقود للوحدة |  | Spasific fuel consumption for power produced | gm/kwh
|  | Spasific fuel consumption for power transmitted | gm/kwh
Startup بيانات الدخول | Cold من الحالة الباردة تحدد الحاله التشغيليه- حسب درجة حرارة جسم التربينه -- ºC > | time required from initial ignition until Synch | Hour | بالتجربة
|  | fuel consumption from initial ignition until Synch | m3 | بالتجربة
|  | Auxilary power consumption from initial ignition until Synch | MWH | فارق قراءة العدادات عمليا + حساب من تقرير استهلاك المساعدات 18 ساعة
|  | Make up water consumption from initial ignition until Synch | m3 | عمليا من التعويض الفعلي خلال فترة الدخول
| Worm من الحالة المتوسطة تحدد الحاله التشغيليه- حسب درجة حرارة جسم التربينه --ºC>T> --ºC | time required from initial ignition until Synch | Hour | بالتجربة
|  | fuel consumption from initial ignition until Synch | m3 | بالتجربة
|  | Auxilary power consumption from initial ignition until Synch | MWH | بالحساب من تقرير استهلاك المساعدات اثناء الوحدة احتياطي
|  | Make up water consumption from initial ignition until Synch | m3 | المقدار في حال الدخول الساخن مضروب في 3 تقريبا
| Hot من الحالة الساخنة -- ºC < | time required from initial ignition until Synch | Hour | بالتجربة
|  | fuel consumption from initial ignition until Synch | m3 | فعلي
|  | Auxilary power consumption from initial ignition until Synch | MWH
|  | Make up water consumption from initial ignition until Synch | m3 | عمليا من التعويض الفعلي خلال فترة الدخول
Shutdown بيانات الخروج | Cold الحالة الباردة | the time required for the unit from the moment of disconnected from the grid until it reaches the cold state | Hour | بالتجربة من ال DCS
|  | the power consumption for the unit from the moment of disconnected from the grid until it reaches the cold state | MWH | بالحساب من تقرير استهلاك المساعدات اثناء الوحدة احتياطي
| الحالة المتوسطة | the time required for the unit from the moment of disconnected from the grid until it reaches the Intermediate state | Hour | بالتجربة من ال DCS
|  | the power consumption for the unit from the moment of disconnected from the grid until it reaches the Intermediate state | MWH | بالحساب من تقرير استهلاك المساعدات اثناء الوحدة احتياطي
Hot Standby (House Load Operation) |  | the unit avaliability to operate on house load | Avail./Not avail.
|  | House Load | MW
Frequency Correction (FC) |  | (FC) (Max. Limitation ) | ±MW
Design Operating Data For Power Plant
Note on G31: calculation
Note on G33: calculation

## Performace Evaluation Data
Period From / / To / / | [5 empty] | Performance Evaluation Data For Power Plant
| Period Time |  | Hr
No | Unit | Company | Type of Power Plant | Maximum Capacity (MW) | Net Capacity (MW) | Total Energy Produced (GWH) | Net energy produced (GWH) | Auxilary Energy Consumption (GWH) |  | Start up Year | No of operating years (year) | Number of actual startups | No of attempets to start up | actual operating time |  | standby down time |  | Forced outage time |  | No of forced outage | time of planned outage (A) |  | time of planned outage (B) | [5 empty] | Fuel Data
[25 empty] | مازوت معادل |  |  |  | Natural Gas |  |  | Mazout |  |  | Regular Diesel |  |  | Special Diesel |  |  | Spasific Fuel Consumption (gm/kwh) | Average fuel cost (SAR/KWH)
[25 empty] | كمية الوقود (طن) | القيمة الحرارية للوقود (ك كالوري/كجم) | Planned derated operation time | Actual derated operation time | Quantity (Million m3) | Calorific valume (Kcal/m3) | Total price (Million SAR) | Quantity (Ton) | Calorific valume (Kcal/kg) | Total price (Million SAR) | Quantity (Million m3) | Calorific valume (Kcal/kg) | Total price (Million SAR) | Quantity (Million m3) | Calorific valume (Kcal/kg) | Total price (Million SAR)
[9 empty] | للمستعمرات |  |  |  |  | Min | Hr | Min | Hr | Min | Hr |  | Min | Hr | Min | Hr |  |  | Hr | Hr
0
0

## Key
Group | Description | symbol
Business Line | Generation BL | G
Business Line | National Grid BL | NG
Business Line | Distribution BL | D
Power Plant Type | Steam Power Plant | ST
Power Plant Type | Combined Cycle PP | CC
Power Plant Type | Gas Power Plant | GT
Equipments | Boiler | B
Equipments | Steam Turbine | T
Equipments | Gas Turbine | T
Equipments | Heat Recovery Steam Gen | HRSG
Equipments | Condenser | Cond
Equipments | Generator | Gen
Equipments | Transformer | Tr
Equipments | Water Treatment System | WT
Equipments | Pump | P
Equipments | Fan | F
Equipments | Compressor | C
Equipments | Valve | V
Equipments | Gear Box | GB
Equipments | Cooling System | CS
Equipments | HVAC System | HVAC
Equipments | Tanks & Vessels | Ta
Equipments | Protection devices | PR
Equipments | Switch Gear, Breakers, MCC | SG
Data Required | Incident Brief description (pre event/ Event/ post event status) | A
Data Required | Operational Data and settings (Actual/Recommended) | B
Data Required | Trend /Alarm / SOE Log of failure | C
Data Required | Equipment Information (Manual/Procedure/Drawings) | D
Data Required | Maintenance Record and Maintenance Plan | E
Data Required | Punch List and outstandig works | F
Data Required | Historical data for similar incident | G
Data Required | Environmental & External Factors | H
Data Required | Human Factors | I
Performance & Audit Data Required | Design Operating Data | P1
Performance & Audit Data Required | Performance Evaluation Data | P2

## Boiler
Data Reqired | Column1 | Column2
Item No | Data | symbol
incident brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | pressure, temperature, and steam flow rate | 1
B | Fuel Type, consumption and efficiency metrics | 2
B | Feed water parameters (pressure, Temp, flow rates) | 3
B | Burner performance and flame characteristics | 4
B | Load variations and plant demand profile | 5
B | Flue gas parameters ( pressure, Temp, flow, analysis,O2,CO2,CO,NOX) | 6
B | feedwater chemistry (pH, conductivity, TDS, oxygen content) | 7
B | Fuel quality (calorific value, moisture, sulfur content) | 8
B | Blowdown water analysis | 9
B | Efficiency losses and heat rate variations | 10
B | Gas Turbine Exhaust Temperature | 11
Trend /Alarm / SOE Log of failure
C | Trends before, during, and after event | 1
C | Alarm Logs and alarm triggered before the Incident | 2
C | protection Settings | 3
C | Sequence of Event before, during and after the incident | 4
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | maintenance History | 1
E | maintenance Plan | 2
E | Recent boiler inspections (corrosion, scaling, erosion, NDT, …etc) | 3
E | Chemical cleaning and descaling schedules and records | 4
E | Past repairs and component replacements | 5
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | trip and alarm history (high temperature, pressure excursions, etc.) | 1
G | Tube Failures (Creep, Fatigue, Corrosion, Erosion) & Header Cracks | 2
G | Gas-side Fouling or Blockage | 3
G | Water/Steam-side Deposits | 4
G | Safety valve operations and pressure relief incidents | 5
G | Operator response times and corrective actions | 6
G | Metallurgical failure analysis of damaged components | 7
G | History of tube failures (Reports,location, type, and frequency) | 8
Environmental & External Factors
H | Ambient temperature and humidity | 1
H | Changes in fuel supply or quality | 2
H | Fuel Quality & Composition | 3
H | Grid demand fluctuations and load variations | 4
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition: Fatigue, stress, distractions. | 6

## Heat Recovery Steam Gen
Data Reqired | Column1 | Column2
Item No | Data | symbol
incident brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | pressure, temperature, and steam flow rate | 1
B | Fuel Type, consumption and efficiency metrics | 2
B | Feed water parameters (pressure, Temp, flow rates) | 3
B | Burner performance and flame characteristics | 4
B | Load variations and plant demand profile | 5
B | Flue gas parameters ( pressure, Temp, flow, analysis,O2,CO2,CO,NOX) | 6
B | feedwater chemistry (pH, conductivity, TDS, oxygen content) | 7
B | Fuel quality (calorific value, moisture, sulfur content) | 8
B | Blowdown water analysis | 9
B | Efficiency losses and heat rate variations | 10
B | Gas Turbine Exhaust Temperature | 11
Trend /Alarm / SOE Log of failure
C | Trends before, during, and after event | 1
C | Alarm Logs and alarm triggered before the Incident | 2
C | protection Settings | 3
C | Sequence of Event before, during and after the incident | 4
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | maintenance History | 1
E | maintenance Plan | 2
E | Recent boiler inspections (corrosion, scaling, erosion, NDT, …etc) | 3
E | Chemical cleaning and descaling schedules and records | 4
E | Past repairs and component replacements | 5
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | trip and alarm history (high temperature, pressure excursions, etc.) | 1
G | Tube Failures (Creep, Fatigue, Corrosion, Erosion) & Header Cracks | 2
G | Gas-side Fouling or Blockage | 3
G | Water/Steam-side Deposits | 4
G | Safety valve operations and pressure relief incidents | 5
G | Operator response times and corrective actions | 6
G | Metallurgical failure analysis of damaged components | 7
G | History of tube failures (Reports,location, type, and frequency) | 8
Environmental & External Factors
H | Ambient temperature and humidity | 1
H | Changes in fuel supply or quality | 2
H | Fuel Quality & Composition | 3
H | Grid demand fluctuations and load variations | 4
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition: Fatigue, stress, distractions. | 6

## Steam Turbine
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | steam pressure, temperature, and steam flow rate at various turbine stages | 1
B | Load variations and plant demand profile, ramp rate | 2
B | Turbine speed and vibration levels | 3
B | Lube oil pressure, temperature | 4
B | Water chemistry and quality (for steam purity) | 5
B | lifting oil pressure and temperature | 6
B | differential expansion and excenterecity | 7
B | Extration steam condition (pressure, temprature, flow) | 8
B | feed water heaters steam and water parameters (P,T, Flow) | 9
B | Efficiency and heat rate degredation (deviation from design value) | 10
Trend /Alarm / SOE Log of failure
C | Trends¦ before, during and after event | 1
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 2
C | Turbine protection settings | 3
C | Sequence of Event before, during and after the Incident | 4
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Turbine maintenance History | 1
E | Turbine maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Lubrication oil condition and oil analysis reports | 4
E | Metallurgical failure analysis of damaged components | 5
E | Blade inspections (erosion, corrosion, fatigue, deposits) | 6
E | Blade and rotor material integrity testing | 7
E | Crack detection and thermal fatigue assessment | 8
E | Foam cleaning and descaling schedules | 9
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Alarm history (high temperature, pressure excursions, etc.) | 1
G | Recorded turbine trips and protection system activations | 2
G | corrective actions have been taken towords the incident | 3
G | History of component failures or abnormalities | 4
Environmental & External Factors
H | Ambient conditions affecting performance (temperature, Winds and flooding) | 1
H | Grid demand fluctuations and load variations | 2
H | Grid Parameters (Frequancy , Voltage) | 3
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Gas Turbine
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Turbine Temperatures: Exhaust gas temperature (EGT), turbine inlet temperature (TIT), combustor exit temperature. | 1
B | Load variations and plant demand profile, ramp rate | 2
B | Turbine speed and vibration levels | 3
B | Lube oil pressure, temperature | 4
B | Fuel Data: Type, composition, heating value, contaminants (e.g., sulfur, vanadium, sodium). | 5
B | lifting oil pressure and temperature | 6
B | differential expansion and excenterecity | 7
B | Pressure Readings: Compressor inlet and discharge pressure, combustor pressure, turbine pressure ratios. | 8
B | Efficiency and heat rate degredation (deviation from design value) | 9
Trend /Alarm / SOE Log of failure
C | Trends¦ before, during and after event | 1
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 2
C | Turbine protection settings | 3
C | Sequence of Event before, during and after the Incident | 4
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Turbine maintenance History | 1
E | Turbine maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Lubrication oil condition and oil analysis reports | 4
E | Metallurgical failure analysis of damaged components | 5
E | Blade inspections (erosion, corrosion, fatigue, crack, deposits, coating degredation, hot spots). | 6
E | Blade and rotor material integrity testing | 7
E | Crack detection and thermal fatigue assessment | 8
E | Borescope Inspection Reports: Findings from internal inspections of hot gas path components. | 9
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Alarm history (high temperature, pressure excursions, etc.) | 1
G | Recorded turbine trips and protection system activations | 2
G | corrective actions have been taken towords the incident | 3
G | History of component failures or abnormalities | 4
Environmental & External Factors
H | Ambient conditions affecting performance (temperature, Winds and flooding) | 1
H | Grid demand fluctuations and load variations | 2
H | Grid Parameters (Frequancy , Voltage, load rejection event) | 3
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Generator
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Load variations and plant demand profile, ramp rate | 2
B | Vibration analysis of bearings, rotor, and stator | 3
B | Bearing temperature and oil condition | 4
B | Power factor and reactive power flow | 5
B | Voltage, current, and power output trends | 6
B | Frequency variations and stability | 7
B | Excitation system performance (voltage regulator settings, field current) | 8
B | Hydrogen or air cooling system pressure, flow, and temperature | 9
B | Water-cooled stator temperature and leakage detection | 10
B | Ventilation system operation and filter condition | 11
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event | 1
C | Alarms triggered before failure (overload, overvoltage, underfrequency, etc.) | 2
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 3
C | Generator protection settings | 4
C | Sequence of Event before, during and after the Incident | 5
C | Relay trip events and protection system activations | 6
C | Ground fault or differential protection activation | 7
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Generator maintenance History | 1
E | Generator maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Stator winding insulation resistance (IR) & polarization index (PI) | 4
E | High-voltage tests (hipot, surge test) | 5
E | Stator and rotor winding continuity and resistance measurements | 6
E | Phase-to-phase and phase-to-ground insulation tests | 7
E | Shaft alignment and coupling integrity | 8
E | Lubrication system performance and oil analysis | 9
E | Brush and slip ring (for synchronous generators) wear condition | 10
E | Rotor dynamic behavior and balance | 11
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Alarm history (Over current, over excitation, over/under freqency … etc.) | 1
G | Recorded generator trips and protection system activations | 2
G | corrective actions have been taken towords the incident | 3
G | History of component failures or abnormalities | 4
G | Long-term performance deviations | 5
Environmental & External Factors
H | Generator cooling water parameters (temperature, pressure, purity) | 1
H | Grid demand fluctuations and load variations | 2
H | Grid Parameters (Frequancy , Voltage) | 3
H | Lightning strikes or system faults | 4
H | Ambient temperature and humidity effects | 5
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Transformer
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Manufacturer, model, and serial number | 1
B | Rating (MVA, kV primary/secondary, impedance, vector group) | 2
B | Date of commissioning and age of the transformer | 3
B | Transformer type (Power, Distribution, Auto, etc.) | 4
B | Cooling method (ONAN, ONAF, OFWF, etc.) | 5
B | Tap changer position and operation history | 6
B | Voltage fluctuations, harmonics, transients | 7
B | Transformer oil and winding temperature trends | 8
B | Differential current values (if available) | 9
B | Restricted Earth Fault (REF) and Buchholz relay status | 10
B | Load variations and plant demand profile, ramp rate | 11
B | Power factor and reactive power flow | 12
B | Voltage, current, and power output trends | 13
B | Bushing condition and insulation integrity | 14
B | Condition of cooling system (radiators, fans, pumps) | 15
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event (voltage, current, load percentage,…etc) | 1
C | Alarms triggered before failure (ovecurrent, overvoltage, bochlez, ...etc.) | 2
C | Any visible signs of damage (burn marks, oil leaks, bulging, cracks) | 3
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 4
C | Transformer protection settings | 5
C | Sequence of Event before, during and after the Incident | 6
C | Relay trip events and protection system activations | 7
C | Ground fault or differential protection activation | 8
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Transformer maintenance History | 1
E | Transformer maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Tap changer maintenance and inspections | 4
E | Cooling system maintenance history | 5
E | Phase-to-phase and phase-to-ground insulation tests | 6
E | Dissolved Gas Analysis (DGA) (H₂, CH₄, C₂H₂, CO, CO₂ levels) | 7
E | Oil quality tests: Moisture content, dielectric strength, acidity | 8
E | Furan analysis: Aging condition of insulation paper | 9
E | Dissolved Gas Analysis (DGA) reports | 10
E | IR (Insulation Resistance) test report | 11
E | Transformer turns ratio (TTR) test report | 12
E | Sweep frequency response analysis (SFRA) report | 13
E | Frequency response analysis (FRA) report | 14
E | Winding resistance test report | 15
E | Capacitance and tan delta tests report | 16
E | Impedance and leakage reactance measurements report | 17
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Recorded Transformer trips and protection system activations | 1
G | corrective actions have been taken towords the incident | 2
G | History of component failures or abnormalities | 3
G | Long-term performance deviations | 4
Environmental & External Factors
H | Lightning strikes, heavy rain, flooding, humidity, temperature. | 1
H | Pollution, dust accumulation | 2
H | Seismic activity or vibrations | 3
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6
9. Grid & System Events
Recent switching events (sudden load changes, faults)
Nearby equipment failures
Transient overvoltage or switching surges

## Pump
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Equipment specifications (manufacturer, model, capacity, type) | 1
B | Equipment operating hours | 2
B | Operating parameters (flow rate, pressure, temperature, efficiency, etc.) | 3
B | Suction and discharge pressure trends | 4
B | Flow rate fluctuations and pressure reading before failure | 5
B | Temperature readings (bearings, motor, casing) | 6
B | Differential pressure across equipment | 7
B | Equipment speed (RPM) | 8
B | Voltage, current, and power consumption trends | 9
B | Lubrication system parameters (oil pressure, temperature, contamination levels)
B | Cooling system data (coolant temperature, flow rate) | 1
B | Motor winding temperatures | 2
B | Circuit breaker and protection system logs | 3
B | Motor start/stop frequency | 4
B | Vibration analysis data | 5
B | Cavitation signs (if any) | 6
B | NPSH (Net Positive Suction Head) calculations | 7
B | Load variations and plant demand profile, ramp rate | 8
B | Any visible signs of damage (burn marks, oil leaks, bulging, cracks) | 9
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event (voltage, current, load percentage,…etc) | 1
C | Description of the failure (symptoms, duration, frequency) | 2
C | Alarms triggered before failure (ovecurrent, overvoltage, bochlez, ...etc.) | 3
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 4
C | Description of the failure (e.g., vibration, leakage, pressure loss, overheating) | 5
C | Sequence of Event before, during and after the Incident | 6
C | Relay trip events and protection system activations | 7
C | Immediate symptoms (noise, excessive vibration, overheating, loss of pressure, etc.) | 8
C | unit demand fluctuations affecting Equipment load | 9
C | How the failure was detected (alarms, inspections, performance degradation) | 10
C | Boiler feed water quality (pH, conductivity, dissolved oxygen levels) | 11
C | Corrective actions taken during or after the failure | 12
C | Valve operation history (any sudden opening/closing causing pressure surges) | 13
C | Photos & videos of damaged parts | 14
C | Debris or foreign material presence | 15
C | Signs of overheating, corrosion, cracks, or misalignment | 16
C | Wear pattern on blades & impeller | 17
C | Comparison with sister units (if applicable) | 18
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Equipment maintenance History | 1
E | Equipment maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Vibration trend analysis (historical vs. before failure) | 4
E | FFT (Fast Fourier Transform) spectrum analysis | 5
E | Shaft misalignment or imbalance data | 6
E | Oil quality tests: Moisture content, dielectric strength, acidity | 7
E | Bearing condition and lubrication records (oil changes, grease application) | 8
E | Blade condition & wear analysis | 9
E | Inspection of casing, seals, and ducts | 10
E | Belt or coupling inspection (if applicable) | 11
E | Motor winding resistance & insulation resistance test results | 12
E | Alignment and balancing record | 13
E | Last lubrication date & type of lubricant used | 14
E | Filter condition & cleaning history | 15
E | Bearing and seal replacement record | 16
E | Motor winding temperature | 17
E | Bearing temperature trends | 18
E | Metallurgical failure analysis (if applicable) | 19
E | Wear and tear on bearings, impellers, and seals | 20
E | Signs of corrosion, erosion, or cavitation damage | 21
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Recorded trips and protection system activations | 1
G | corrective actions have been taken towords the incident | 2
G | History of component failures or abnormalities | 3
G | Long-term performance deviations | 4
Environmental & External Factors
H | Ambient temperature and humidity at the time of failure | 1
H | Quality of intake air (dust, moisture, contaminants) | 2
H | Load variations & plant operating conditions | 3
H | Grid disturbances or power issues | 4
H | Recent changes in operating procedures | 5
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Fan
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Equipment specifications (manufacturer, model, capacity, type) | 1
B | Equipment operating hours | 2
B | Operating parameters (flow rate, pressure, temperature, efficiency, etc.) | 3
B | Suction and discharge pressure trends | 4
B | Flow rate fluctuations and pressure reading before failure | 5
B | Temperature readings (bearings, motor, casing) | 6
B | Differential pressure across equipment | 7
B | Equipment speed (RPM) | 8
B | Voltage, current, and power consumption trends | 9
B | Lubrication system parameters (oil pressure, temperature, contamination levels) | 10
B | Cooling system data (coolant temperature, flow rate) | 11
B | Motor winding temperatures | 12
B | Circuit breaker and protection system logs | 13
B | Motor start/stop frequency | 14
B | Vibration analysis data | 15
B | Cavitation signs (if any) | 16
B | NPSH (Net Positive Suction Head) calculations | 17
B | Load variations and plant demand profile, ramp rate | 18
B | Any visible signs of damage (burn marks, oil leaks, bulging, cracks) | 19
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event (voltage, current, load percentage,…etc) | 1
C | Description of the failure (symptoms, duration, frequency) | 2
C | Alarms triggered before failure (ovecurrent, overvoltage, bochlez, ...etc.) | 3
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 4
C | Description of the failure (e.g., vibration, leakage, pressure loss, overheating) | 5
C | Sequence of Event before, during and after the Incident | 6
C | Relay trip events and protection system activations | 7
C | Immediate symptoms (noise, excessive vibration, overheating, loss of pressure, etc.) | 8
C | unit demand fluctuations affecting Equipment load | 9
C | How the failure was detected (alarms, inspections, performance degradation) | 10
C | Boiler feed water quality (pH, conductivity, dissolved oxygen levels) | 11
C | Corrective actions taken during or after the failure | 12
C | Valve operation history (any sudden opening/closing causing pressure surges) | 13
C | Photos & videos of damaged parts | 14
C | Debris or foreign material presence | 15
C | Signs of overheating, corrosion, cracks, or misalignment | 16
C | Wear pattern on blades & impeller | 17
C | Comparison with sister units (if applicable) | 18
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Equipment maintenance History | 1
E | Equipment maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Vibration trend analysis (historical vs. before failure) | 4
E | FFT (Fast Fourier Transform) spectrum analysis | 5
E | Shaft misalignment or imbalance data | 6
E | Oil quality tests: Moisture content, dielectric strength, acidity | 7
E | Bearing condition and lubrication records (oil changes, grease application) | 8
E | Blade condition & wear analysis | 9
E | Inspection of casing, seals, and ducts | 10
E | Belt or coupling inspection (if applicable) | 11
E | Motor winding resistance & insulation resistance test results | 12
E | Alignment and balancing record | 13
E | Last lubrication date & type of lubricant used | 14
E | Filter condition & cleaning history | 15
E | Bearing and seal replacement record | 16
E | Motor winding temperature | 17
E | Bearing temperature trends | 18
E | Metallurgical failure analysis (if applicable) | 19
E | Wear and tear on bearings, impellers, and seals | 20
E | Signs of corrosion, erosion, or cavitation damage | 21
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Recorded trips and protection system activations | 1
G | corrective actions have been taken towords the incident | 2
G | History of component failures or abnormalities | 3
G | Long-term performance deviations | 4
Environmental & External Factors
H | Ambient temperature and humidity at the time of failure | 1
H | Quality of intake air (dust, moisture, contaminants) | 2
H | Load variations & plant operating conditions | 3
H | Grid disturbances or power issues | 4
H | Recent changes in operating procedures | 5
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Compressor
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Equipment specifications (manufacturer, model, capacity, type) | 1
B | Equipment operating hours | 2
B | Operating parameters (flow rate, pressure, temperature, efficiency, etc.) | 3
B | Suction and discharge pressure trends | 4
B | Flow rate fluctuations and pressure reading before failure | 5
B | Temperature readings (bearings, motor, casing) | 6
B | Differential pressure across equipment | 7
B | Equipment speed (RPM) | 8
B | Voltage, current, and power consumption trends | 9
B | Lubrication system parameters (oil pressure, temperature, contamination levels) | 10
B | Cooling system data (coolant temperature, flow rate) | 11
B | Motor winding temperatures | 12
B | Circuit breaker and protection system logs | 13
B | Motor start/stop frequency | 14
B | Vibration analysis data | 15
B | Cavitation signs (if any) | 16
B | NPSH (Net Positive Suction Head) calculations | 17
B | Load variations and plant demand profile, ramp rate | 18
B | Any visible signs of damage (burn marks, oil leaks, bulging, cracks) | 19
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event (voltage, current, load percentage,…etc) | 1
C | Description of the failure (symptoms, duration, frequency) | 2
C | Alarms triggered before failure (ovecurrent, overvoltage, bochlez, ...etc.) | 3
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 4
C | Description of the failure (e.g., vibration, leakage, pressure loss, overheating) | 5
C | Sequence of Event before, during and after the Incident | 6
C | Relay trip events and protection system activations | 7
C | Immediate symptoms (noise, excessive vibration, overheating, loss of pressure, etc.) | 8
C | unit demand fluctuations affecting Equipment load | 9
C | How the failure was detected (alarms, inspections, performance degradation) | 10
C | Boiler feed water quality (pH, conductivity, dissolved oxygen levels) | 11
C | Corrective actions taken during or after the failure | 12
C | Valve operation history (any sudden opening/closing causing pressure surges) | 13
C | Photos & videos of damaged parts | 14
C | Debris or foreign material presence | 15
C | Signs of overheating, corrosion, cracks, or misalignment | 16
C | Wear pattern on blades & impeller | 17
C | Comparison with sister units (if applicable) | 18
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Equipment maintenance History | 1
E | Equipment maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Vibration trend analysis (historical vs. before failure) | 4
E | FFT (Fast Fourier Transform) spectrum analysis | 5
E | Shaft misalignment or imbalance data | 6
E | Oil quality tests: Moisture content, dielectric strength, acidity | 7
E | Bearing condition and lubrication records (oil changes, grease application) | 8
E | Blade condition & wear analysis | 9
E | Inspection of casing, seals, and ducts | 10
E | Belt or coupling inspection (if applicable) | 11
E | Motor winding resistance & insulation resistance test results | 12
E | Alignment and balancing record | 13
E | Last lubrication date & type of lubricant used | 14
E | Filter condition & cleaning history | 15
E | Bearing and seal replacement record | 16
E | Motor winding temperature | 17
E | Bearing temperature trends | 18
E | Metallurgical failure analysis (if applicable) | 19
E | Wear and tear on bearings, impellers, and seals | 20
E | Signs of corrosion, erosion, or cavitation damage | 21
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Recorded trips and protection system activations | 1
G | corrective actions have been taken towords the incident | 2
G | History of component failures or abnormalities | 3
G | Long-term performance deviations | 4
Environmental & External Factors
H | Ambient temperature and humidity at the time of failure | 1
H | Quality of intake air (dust, moisture, contaminants) | 2
H | Load variations & plant operating conditions | 3
H | Grid disturbances or power issues | 4
H | Recent changes in operating procedures | 5
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Valve
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Valve type: Gate, globe, check, control, safety, etc. | 1
B | Valve location: Main steam line, bypass, condenser, turbine, boiler feedwater, etc. | 2
B | Operating conditions: Temperature, upsteam and downstream pressure, flow rate, steam quality. | 3
B | manufacturer, model, material, specifications. | 4
B | Flow rate fluctuations that might indicate obstruction. | 5
B | Pressure drop across the valve | 6
B | Differential pressure across equipment | 7
B | Cycle count & operation frequency: High-cycle fatigue or thermal stress. | 8
B | Water quality & chemical treatment records: Presence of contaminants. | 9
B | Signs of overheating or erosion | 10
B | Stuck or sluggish movement | 11
B | Unusual noise or vibration | 12
B | Valve not opening/closing properly | 13
B | Leakage (internal/external) | 14
B | Erosion or cavitation damage: Steam impingement, flashing issues. | 15
B | Thermal expansion effects: Expansion/contraction stresses. | 16
B | Actuator or control signal failure: Pneumatic, electric, hydraulic. | 17
B | Load variations and plant demand profile, ramp rate | 18
B | Any visible signs of damage (burn marks, oil leaks, bulging, cracks) | 19
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event (opening %, flow, pressure, temp…etc) | 1
C | Description of the failure (symptoms, duration, frequency) | 2
C | Alarms triggered before failure. | 3
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 4
C | Description of the failure. | 5
C | Sequence of Event before, during and after the Incident | 6
C | unit demand fluctuations affecting Equipment load | 7
C | Corrective actions taken during or after the failure | 8
C | Valve operation history (any sudden opening/closing causing pressure surges) | 9
C | Photos & videos of damaged parts | 10
C | Signs of overheating, corrosion, cracks, or misalignment | 11
C | Valve position history: Stuck open/closed, partial movement. | 12
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
Maintenance History& Maintenance Plan
E | Equipment maintenance History | 1
E | Equipment maintenance Plan | 2
E | inspection details: Date, method (visual, ultrasonic, etc.). | 3
E | Lubrication history: Frequency and type of lubricant used. | 4
E | Seal and packing condition: Signs of wear, leaks, or blowout. | 5
E | Fasteners & actuator condition: Loose bolts, misalignment, rust. | 6
E | Corrosion & scaling evidence: Deposits, rust, or chemical attack. | 7
E | Material defects: Cracks, pitting, embrittlement. | 8
E | Non-destructive testing (NDT): Ultrasonic, radiographic, magnetic particle inspection. | 9
E | Metallurgical analysis: Material composition, microstructure defects. | 10
E | Last lubrication date & type of lubricant used | 11
E | Filter condition & cleaning history | 12
E | Bearing and seal replacement record | 13
E | Motor winding temperature | 14
E | Bearing temperature trends | 15
E | Metallurgical failure analysis (if applicable) | 16
E | Wear and tear on bearings, impellers, and seals | 17
E | Signs of corrosion, erosion, or cavitation damage | 18
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Recorded trips and protection system activations | 1
G | corrective actions have been taken towords the incident | 2
G | History of component failures or abnormalities | 3
G | Long-term performance deviations | 4
Environmental & External Factors
H | Ambient temperature and humidity at the time of failure | 1
H | Vibration from adjacent machinery. | 2
H | Load variations & plant operating conditions | 3
H | External mechanical impacts. | 4
H | Chemical exposure from nearby processes. | 5
H | Recent changes in operating procedures | 6
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Sequence of actions before failure (manual overrides, setpoint changes). Delayed response | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Cooling System
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
A | incident Brief Desciption
A | Date and time of failure | 1
A | Pre- Incident condition | 2
A | Incident Condition | 3
A | After-Incident condition | 4
A | Coorective action taken | 5
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 6
Operational Data and settings (Actual/Recommended)
B | Coolant type (e.g., hydrogen, deionized water, air) | 1
B | Hydrogen purity and pressure levels (if applicable) | 2
B | Cooling water inlet/outlet temperatures and pressures | 3
B | Flow rate of cooling medium | 4
B | Heat exchanger performance data | 5
B | Pressure drop across filters and heat exchanger | 6
B | Water chemistry analysis (pH, conductivity, dissolved oxygen, contaminants) | 7
B | Signs of overheating or erosion | 8
B | Cooling system piping and valve condition (blockages, leaks, corrosion) | 9
B | Heat exchanger fouling or efficiency drop | 10
B | Pump data (flow, pressure, power consumption) | 11
B | Fan or blower condition (if air-cooled) | 12
B | Valve Performance: Blockage, leakage, or malfunction | 13
B | Leakage (internal/external) | 14
B | Microbiological Growth: Presence of biofouling or microbial corrosion | 15
B | Contaminant Analysis: Oil ingress, particulate matter, dissolved gases (O₂, CO₂) | 16
B | Erosion, scaling or cavitation damage. | 17
B | Thermal expansion effects: Expansion/contraction stresses. | 18
B | Load variations and plant demand profile, ramp rate | 19
B | Any visible signs of damage (leaks, bulging, cracks) | 20
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event ( flow, pressure, temp…etc) | 1
C | Description of the failure (symptoms, duration, frequency, alarm triggered) | 2
C | Alarms triggered before failure. | 3
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 4
C | Description of the failure. | 5
C | Sequence of Event before, during and after the Incident | 6
C | unit demand fluctuations affecting Equipment load | 7
C | System affected (e.g., hydrogen cooling, water cooling, air cooling) | 8
C | operation history (any sudden opening/closing causing pressure surges) | 9
C | Photos & videos of damaged parts | 10
C | Signs of overheating, corrosion, cracks, or leakage | 11
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & PIDs | 4
D | Flow rate and heat exchanger performance data | 5
D | Cooling tower/chiller specifications (if applicable) | 6
Maintenance History& Maintenance Plan
E | Equipment maintenance History | 1
E | Equipment maintenance Plan | 2
E | inspection details: Date, method (visual, ultrasonic, etc.). | 3
E | Hydrogen seal and leakage test results (for hydrogen-cooled systems) | 4
E | Seal and packing condition: Signs of wear, leaks, or blowout. | 5
E | Fasteners & actuator condition: Loose bolts, misalignment, rust. | 6
E | Corrosion & scaling evidence: Deposits, rust, or chemical attack. | 7
E | Material defects: Cracks, pitting, embrittlement. | 8
E | Non-destructive testing (NDT): Ultrasonic, radiographic, magnetic particle inspection. | 9
E | Metallurgical analysis: Material composition, microstructure defects. | 10
E | Last lubrication date & type of lubricant used | 11
E | Filter condition & cleaning history | 12
E | Bearing and seal replacement record | 13
E | Motor winding temperature | 14
E | Bearing temperature trends | 15
E | Metallurgical failure analysis (if applicable) | 16
E | Wear and tear on bearings, impellers, and seals | 17
E | Signs of corrosion, erosion, or cavitation damage | 18
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Recorded trips and protection system activations | 1
G | corrective actions have been taken towords the incident | 2
G | Comparing with historical trends to identify anomalies | 3
G | Past similar failures in the same plant or other units | 4
Environmental & External Factors
H | Ambient temperature,humidity, and weather condition at the time of failure | 1
H | Vibration from adjacent machinery. | 2
H | any change in plant Load or plant operating conditions | 3
H | External mechanical impacts. | 4
H | Chemical exposure from nearby processes. | 5
H | Recent maintenance or modifications in the cooling system | 6
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Sequence of actions before failure (manual overrides, setpoint changes). Delayed response | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## grid problem
Data Reqired | Column1 | Column2
Item No | Data | Required (Y/N)
incident Brief Desciption
A | Date and time of grid disturbance | 1
A | Type of Event (e.g., blackout, frequency fluctuation, voltage sag, equipment failure) | 2
A | Pre- Incident condition | 3
A | Incident Condition | 4
A | After-Incident condition | 5
A | Duration of the event | 6
A | Coorective action taken | 7
A | Impact on plant operations (downtime, efficiency loss, fuel consumption during outage period, Auxulary power consumption during outage period, sent power loss ) | 8
Operational Data and settings (Actual/Recommended)
B | Load variations and plant demand profile, ramp rate | 1
B | Power factor and reactive power flow | 2
B | Voltage, current, and power output trends | 3
B | Frequency variations and stability | 4
B | Excitation system performance (voltage regulator settings, field current) | 5
B | Fuel Consumption and unit performance parameters | 6
B | Generator Protection System Logs (trips, alarms, and faults) | 7
B | Turbine & Boiler Performance Data (for thermal plants) | 8
B | SCADA/EMS Logs capturing real-time plant behavior | 9
B | Generator protection settings | 10
Trend /Alarm / SOE Log of failure
C | Trends before, during and after event | 1
C | Alarms triggered before failure (overload, overvoltage, underfrequency, etc.) | 2
C | DCS (Distributed Control System) and PLC (Programmable Logic Controller) event logs. | 3
C | Sequence of Event before, during and after the Incident | 4
C | Grid Frequency Variations before, during, and after the incident | 5
C | Voltage Profile at plant interconnection and nearby substations | 6
C | Reactive Power Flow and power factor trends | 7
C | Load Shedding Events and demand changes | 8
C | Fault Reports from Transmission/Distribution operators | 9
C | Relay Operation Logs (time-stamped protection activations) | 10
C | Breaker Operation Logs (which breakers operated and their sequence) | 11
C | Under-Frequency/Voltage Protection Data | 12
C | ROCOF (Rate of Change of Frequency) Events | 13
C | SCADA/EMS Operator Actions (manual interventions or automation) | 14
C | RTU (Remote Terminal Unit) or PLC Data Logs | 15
C | Inter-Utility Coordination Logs (exchange of information with grid operators) | 16
Equipment Information (Manual/Procedure/Drawings)
D | Equipment Manual | 1
D | Process Procedure | 2
D | System Discribtion | 3
D | Drawings & SLD | 4
Maintenance History& Maintenance Plan
E | Generator maintenance History | 1
E | Generator maintenance Plan | 2
E | Major maintenance activities (overhauls, repairs, replacements) | 3
E | Recent Maintenance or Upgrades (before the event) | 4
E | Equipment Failures or Alarms (transformers, switchgear, generators) | 5
E | Aging & Condition of Components (cables, busbars, protection devices) | 6
Punch List and outstanding works
F | Punch List and incomplete Commissioing works | 1
F | Actions have Taken to close the open points and outstanding Items | 2
Historical data for similar incident
G | Alarm history (Over current, over excitation, over/under freqency … etc.) | 1
G | Recorded generator trips and protection system activations | 2
G | corrective actions have been taken towords the incident | 3
G | History of component failures or abnormalities | 4
Environmental & External Factors
H | Weather Reports (lightning strikes, storms, temperature variations) | 1
H | Natural Disasters (earthquakes, floods, cyclones) | 2
H | Cybersecurity Events (if any abnormal network activity was detected) | 3
Human Factors
I | Involved Personnel roles, experience, certifications. | 1
I | Operator Actions: Sequence of actions before failure (manual overrides, setpoint changes). | 2
I | Task Being Performed Standard operating procedure (SOP) followed or not. | 3
I | Fatigue & Workload: Shift hours, overtime records, workload at the time. | 4
I | Training Records: Relevant training history, refresher courses. | 5
I | Physical & Mental Condition | 6

## Collected Data
Data Required | Control System | Boiler | Column1 | Steam Turbine | Column2 | Condenser | Gas Turbine | HRSG | Generator | Transformer | Pump | Fan | Valve | Compressor | Tanks | Cooling System | Water Treatment | Water Desalination | Switch Gear | Protection Relay | Column16 | Column17
(A) Equipment Information
1 |  | Boiler pressure, temperature, and steam flow rate | a
2 |  | Fuel Type, consumption and efficiency metrics
3 |  | Feed water parameters (pressure, Temp, flow rates)
4 |  | Burner performance and flame characteristics | a
5 |  | Load variations and plant demand profile
6 |  | Flue gas parameters ( pressure, Temp, flow, analysis) | a
(B) maintenance and inspection Record
1 |  | Boiler tube metal temperatures
2 |  | Boiler efficiency and fouling factors
3 |  | History of tube failures (location, type, and frequency)
4 |  | Recent boiler inspections (corrosion, scaling, erosion)
5 |  | Turbine and generator maintenance logs
6 |  | Chemical cleaning and descaling schedules
7 |  | Past repairs and component replacements

## examble
Form | Business Line - Power Plant Type - Equipment - Data Req-No
Exaple | G-ST-B-A-1
Data Required From GBL for RCA (PP13 Outage Incident Dated 15/2/2025)
Item # | Item Description | Received
Yes/No
G-ST-B-A-1
G-ST-B-A-2
G-ST-B-A-3
G-ST-B-A-4
G-ST-B-A-5
G-ST-B-A-6
G-ST-B-A-7
G-ST-B-A-8
G-ST-B-A-4
G-ST-B-B-1
G-ST-B-B-2
G-ST-B-B-3
G-ST-B-B-4
G-ST-B-C-1
G-ST-B-C-2
G-ST-B-C-3
G-ST-B-D-1